Connection Detail

Terminal	Function

1:		To Positive of Battery

2:		To Positive of LED

3:		To Negative of Battery & LED -

Mechanical & Technical Specification.

Weight:		Approx 5 Gram's

Height:		15mm.

Width:	 	33mm

Depth:		55mm

Colour:		PCB

IP Rating:	N/A

Trip Point Stability:	+/-1%

Trip Adjustment:		+/-15% of nominal

Typical Applications.

DC Supply Low Voltage Warning!

Available for 12 or 24 operation!

Audio Battery Supply Voltage Monitoring!

Protect Batteries from excessive discharge!

Charger failure warning device!

Can be configured to drive external relay!

Designed for OEM and DIY applications!

The CBC 822 Low Battery indicator is a solid state device that measures the dc supply from which it is powered and energises an led if the potential falls below a pre-set level. The standard unit consists of a printed circuit board, adjustment potentiometer and monitoring circuit. A Relay driver option is also available as an alternative to the led if required.

A fixed delay in included which is normally approximately 60 seconds and stops the led from lighting up until the low level has been present for the delay time period. This allows the unit to operate on engine starting or switch tripping battery installations.

The unit functions by measuring the dc voltage through a potential divider and comparing it to a fixed reference using an amplifier. If the measured potential falls below the reference voltage depending upon the model, the amplifier output switches from low to high, which energises the led. The unit is completely self contained and easy to connect using just two supply cables. Reverse polarity protection is provided using a number of high voltage diodes.

The pcb is designed for OEM applications and must be mounted in a suitable enclosure such as a plastic box to protect the components from moisture and/or damage.

The Low Battery indicators configured to operate on a fixed number of lead-acid cells or the nickel-cadmium equivalent. The trip level is pre-set but can be adjusted by the end user to suit a wide range of applications.

Adjustments are made using the potentiometer mounted on the top face of the pcb. Simply connect the unit to a DC power supply pre-set to the required trip voltage and slowly adjust the potentiometer until the led illuminates.

The 822 Low Battery indicator will operate over a wide temperature range resulting in a unit that can be used in leisure, marine and industrial applications.

Data Sheet Number LBI-01-02

822 LOW BATTERY INDICATOR

Design & Operating Characteristics

CBC Design.

12 Jubilee Place, Clevedon,

UK. BS21 5EA.

Tel 07768 206649

Fax 01275 878362

Supplier:

CBC Design. Controller & Battery Charger Fabrication Refurbishment & Repairs.

12 Jubilee Place, Clevedon, North Somerset. BS21 5EA. Tel 07768 206649

http://www.cbcdesign.co.uk