The CBCCFM-667-1 Charge Failure Monitor is a solid state device which monitors current flow and trips a normally energised relay if it falls below a pre-set level. The unit is dc powered and consists of a printed circuit board that is fixed to an eleven-pin base and protected by a black dustproof cover.

The unit functions by measuring the output from a current transformer through a potential divider and comparing it to a fixed reference using an amplifier. If the current signal voltage falls below the reference voltage, the amplifier output switches from high to low, which triggers a timer. Once the timing period (pre-set) has elapsed, the normally energised PCB mounted relay de-energises and the voltfree contacts connected to the eleven pin socket change state. Reverse polarity protection is provided using a number of high voltage diodes.

The monitor has been designed to plug into a standard eleven pin octal base. This enables the unit to be easily withdrawn for recalibration or replaced in the unlikely event of failure.

The Charge Failure Monitors are configured to operate on a fixed number of lead-acid cells or the nickel-cadmium equivalent. The trip level is pre-set to <30mA dc as is the delay between fault detection and relay de-energisation.

As well as detecting relatively small current levels, the CFM can also be configured to detect high current levels. This enables the unit to operate as an overload or current limit monitor.

On board led indicators are fitted to the unit. Both LED's illuminate through the product label which is fixed to the top of the dust proof cover. The red led labelled " CHARGE FAIL" illuminates when the monitor detects a low current condition. The green led illuminates when the monitor is in a "HEALTHY" condition.

Data Sheet Number CFM-02/15

CHARGE

FAILURE

MONITORS

Design & Operating Characteristics

Connection Detail

Base No		Function (de-energised mode)

1.		Common Contact RL1/A

2.		Battery/DC Negative

3.		Open Contact RL1/A

4.		Closed Contact RL1/A

5.		Current Transformer Input

6.		Do Not Connect

7.		Do Not Connect

8.		Closed Contact RL1/B

9.		Open Contact RL1/B

10		Battery/DC Positive

11		Common Contact RL1/B

Mechanical & Technical Specification.

Weight:		96 Gram's

Height:		90mm Including pins

Width:	 	50mm

Depth:		50mm

Trip Point Stability:	+/-1%

Trip Adjustment:		+/-10% of nominal

Standard Delay:		60 Seconds

Delay range:		50-130 Seconds

Longer delay periods can be achieved by changing the components around the timer as required. Contact your supplier for further information.

CBC Design.

12 Jubilee Place, Clevedon,

UK. BS21 5EA.

Tel 07768 206649

Fax 01275 878362

Supplier:

CBC Design. Controller & Battery Charger Fabrication Refurbishment & Repairs.

12 Jubilee Place, Clevedon, North Somerset. BS21 5EA. Tel 07768 206649.

http://www.cbcdesign.co.uk