The CBCLVM-667-1 Low Voltage Monitor is a solid state device that measures the dc supply from which it is powered and trips a normally energised relay if the potential falls below a pre-set level. The unit consists of a printed circuit board that is fixed to an eleven-pin base and protected by a black dustproof cover.

The unit functions by measuring the dc voltage through a potential divider and comparing it to a fixed reference using an amplifier. If the measured potential falls below the reference voltage, the amplifier output switches from high to low, which triggers a timer. Once the timing period (pre-set) has elapsed, the normally energised PCB mounted relay de-energises and the voltfree contacts connected to the eleven pin socket change state. Reverse polarity protection is provided using a number of high voltage diodes.

The monitor has been designed to plug into a standard eleven pin octal base. This enables the unit to be easily withdrawn for recalibration or replaced in the unlikely event of failure.

The Low Volts Monitors are configured to operate on a fixed number of lead-acid cells or the nickel-cadmium equivalent. The trip level is pre-set, as is the delay between fault detection and relay de-energisation.

A secondary trip potential can be initiated by connecting pin 7 to pin 2. This enables the monitors to detect two separate voltage trip points such as low dc volts or end of discharge.

On board led indicators are fitted to the unit. Both LED's illuminate through the product label which is fixed to the top of the dust proof cover. The red led labelled " LOW VOLTS" illuminates when the monitor detects a low voltage condition. The green led illuminates when the monitor is in a "HEALTHY" condition.

Data Sheet Number LVM-02/15

LOW DC VOLTAGE MONITORS

Design & Operating Characteristics

Connection Detail

Base No		Function (de-energised mode)

1.		Common Contact RL1/A

2.		Battery/DC Negative

3.		Open Contact RL1/A

4.		Closed Contact RL1/A

5.		Do Not Connect

6.		Do Not Connect

7.		Secondary Trip

8.		Closed Contact RL1/B

9.		Open Contact RL1/B

10		Battery/DC Positive

11		Common Contact RL1/B

Mechanical & Technical Specification.

Weight:		96 Gram's

Height:		90mm Including pins

Width:	 	50mm

Depth:		50mm

Trip Point Stability:	+/-1%

Secondary Trip Stability:	+/-1%

Trip Adjustment:		+/-10% of nominal

Standard Delay:		60 Seconds

Delay range:		50-130 Seconds

Longer delay periods can be achieved by changing the components around the timer as required. Contact your supplier for further information.

CBC Design.

12 Jubilee Place, Clevedon,

UK. BS21 5EA.

Tel 07768 206649

Fax 01275 878362

Supplier:

CBC Design. Controller & Battery Charger Fabrication Refurbishment & Repairs.

12 Jubilee Place, Clevedon, North Somerset. BS21 5EA. Tel 07768 206649

http://www.cbcdesign.co.uk