Enclosed industrial battery chargers are solid state units designed to recharge a fixed number of lead-acid or nickel cadmium batteries. The units are built into industrial grade mild steel enclosures finished in RAL7032 light grey. Special colours are available upon request.

The charger functions by measuring the battery voltage and delivering as much current as the battery require up to the electronically limited maximum. As the battery approaches the fully charged voltage, the current is gradually reduced until the flow out of the controller matches the discharge from the battery. The float voltage (fully charged potential) control amplifier has a tolerance of +/-1%. Temperature compensation or Boost is sometimes provided. The current limit amplifier has a tolerance of +/-2%. The DC charging current is measured using a shunt or AC current transformer through which one of the mains transformer secondary wires must pass.

The charger is mounted using the fixing brackets provided on the back of the enclosure. Connections to and from the unit are available on the terminal strip mounted on the top face of the backplate. Connection instructions are provided with the goods but extra copies may be obtained from your supplier should you require them.

Units are configured to operate on a fixed number of cells including lead-acid or nickel-cadmium. The current limit is pre-set to suit the type of battery connected and should not be adjusted. Altering the current limit may overload the charger.

Both AC and DC fusing are included with every charging system providing overload, short circuit and reverse polarity protection. The fuses can be substituted for MCB’s if required.

Additional items such as Auto Boost, voltage and current monitors can be fitted as optional extras.

Data Sheet Number CDT686-01/99

ENCLOSED
INDUSTRIAL BATTERY
CHARGERS.

Design & Operating Characteristics

Mechanical & Technical Specification.

Model			Height	Width	Depth

CDT686-5A12V		400mm	300mm	200mm

CDT686-5A24V		400mm	300mm	200mm

CDT686-5A30V		500mm	400mm	200mm

CDT686-5A48V		500mm	400mm	200mm

CDT686-5A110V	600mm	500mm	250mm

CDT686-10A12V	500mm	400mm	200mm

CDT686-10A24V	500mm	400mm	200mm

CDT686-10A30V	500mm	400mm	200mm

CDT686-10A48V	600mm	500mm	250mm

CDT686-10A110V	800mm	600mm	250mm

CDT686-20A12V	500mm	400mm	200mm

CDT686-20A24V	600mm	500mm	250mm

CDT686-20A30V	600mm	500mm	250mm

CDT686-20A48V	800mm	600mm	250mm

CDT686-20A110V	1000mm	1000mm	300mm

CDT686-30A12V	800mm	600mm	250mm

CDT686-30A24V	1000mm	1000mm	300mm

CDT686-30A48V	1000mm	1000mm	300mm

CDT686-30A110V	1200mm	1000mm	300mm

Other sizes available upon request.

Float Stability:		+/-1%

Boost Stability:		+/-1%

Current Stability:		+/-2%

Float Adjustment:	+/-10% of nominal

Current Adjustment:	5-100% of rating

Output Ripple:		Approx 12%RMS.

Inductive filters can be fitted in series with the output from the controllers to limit the ripple to less than 1%. This will increase the cubicle dimensions which, can be provided upon request.

CBC Design.

12 Jubilee Place, Clevedon,

UK. BS21 5EA.

Tel 07768 206649

Fax 01275 878362

Supplier:

CBC Design. Controller & Battery Charger Fabrication Refurbishment & Repairs.

12 Jubilee Place, Clevedon, North Somerset. BS21 5EA. Tel 07768 206649

http://www.cbcdesign.co.uk